## Total Project BoQ
LITB-2026-9205634- Localized Water Supply System at IDP Camps
ITEM No | DESCRIPTION | UNIT | Total QTY. | Unit Price- ILS | TOTAL Price-ILS
1 | Piping Works
1.1 | Supply PE drinking water hose pipes 75mm diameter, PN10 (including connecting joints). | LM | 3300 |  | 0
1.2 | Supply PE drinking water hose pipes 50mm diameter, PN10 (including connecting joints). | LM | 20600 |  | 0
1.3 | Supply PE drinking water hose pipes 32mm diameter, PN10 (including connecting joints). | LM | 12650 |  | 0
1.4 | Supply PE drinking water hose pipes 25mm diameter, PN10 (including connecting joints). | LM | 6350 |  | 0
1.5 | Supply PE drinking water hose pipes 20mm diameter, PN10 (including connecting joints). | LM | 4300 |  | 0
Total Piping Works |  |  |  |  | 0
2 | Fittings Works
2.1 | Supply Brass Ball Valve 75 mm, PN16, with all fitting needed to connection at pipe. | No. | 9 |  | 0
2.2 | Supply Brass Ball Valve 50 mm, PN16, with all fitting needed to connection at pipe. | No. | 128 |  | 0
2.3 | Supply Brass Ball Valve 32 mm, PN16, with all fitting needed to connection at pipe. | No. | 559 |  | 0
2.4 | Supply Brass Ball Valve 25 mm, PN16, with all fitting needed to connection at pipe. | No. | 595 |  | 0
2.5 | Supply Brass Ball Valve 20 mm, PN16, with all fitting needed to connection at pipe. | No. | 362 |  | 0
2.6 | Supply and installation of 25 mm Brass Ball Valve, PN16, including all necessary fittings for connection, and installation galvanized steel pipe, L=1 m length, diameter 3/4", complete with elbow and 25 mm male adaptor, with fixing support stand, including all and accessories required for proper installation and stability. | No. | 308 |  | 0
2.6 | Supply PE Clamp saddle 75/50mm,with reinforced stainless steel ring and stainless steel bolts and nut, PN16 (including Male adaptor 32mm, PN16). | No | 84 |  | 0
2.7 | Supply PE Clamp saddle 75/32mm,with reinforced stainless steel ring and stainless steel bolts and nut, PN16 (including Male adaptor 32mm, PN16). | No | 161 |  | 0
2.8 | Supply PE Clamp saddle 50/32mm,with reinforced stainless steel ring and stainless steel bolts and nut, PN16 (including Male adaptor 32mm, PN16). | No | 139 |  | 0
2.9 | Supply PE Clamp saddle 50/25mm, with reinforced stainless steel ring and stainless steel bolts and nut, PN16 (including Male adaptor 25mm, PN16). | No | 269 |  | 0
2.10 | Supply PE Clamp saddle 50/20mm, with reinforced stainless steel ring and stainless steel bolts and nut, PN16 (including Male adaptor 25mm, PN16). | No | 710 |  | 0
2.11 | Supply PE Tee 75/75mm, PN10. | No | 12 |  | 0
2.12 | Supply PE Tee 50/50mm, PN10. | No | 144 |  | 0
2.13 | Supply PE Tee 32/32mm, PN10. | No | 242 |  | 0
2.14 | Supply PE Tee 32/20mm, PN10. | No | 211 |  | 0
2.15 | Supply PE end cap 75mm, PN10. | No | 30 |  | 0
2.16 | Supply PE end cap 50mm, PN10. | No | 156 |  | 0
2.17 | Supply PE end cap 32mm, PN10. | No | 83 |  | 0
2.18 | Supply PE end cap 25mm, PN10. | No | 98 |  | 0
Total Fitting Work |  |  |  |  | 0
3 | Manholes Work
3.1 | Plastic PE Manhole Set – DN600: Supply complete DN600 plastic manhole sets, each comprising DN600 × 600 mm high plastic manhole base, with five (5) factory-moulded inlet connections and one outlet connection suitable for DN110–160 mm pipes; DN600 × 200 mm high elevation ring; DN600 element/ring seal for watertight connection between manhole sections; and DN600 plastic manhole cover with matching frame, Load Class A15. The manhole base and elevation ring shall be manufactured from high-quality, corrosion- and chemical-resistant polyethylene/plastic suitable for underground applications. The complete set shall include all required seals, fittings, connectors and accessories necessary for proper assembly and watertight connection of the components. | No | 68 |  | 0
4 | Water Tanks
4.1 | Supply rigid polyethylene (PE) drinking water storage tank, 5000 liters capacity, food-grade, UV-stabilized, suitable for potable water storage, complete with float valve, overflow pipe (2”diam), lid, outlet ball valve 2", threaded adaptor 2"- male/female as required to suit the tank outlet and connected fittings- , and standard fittings, and all connections for rising main and distribution pipes, including all accessories and approved quality, including painting tanks with white oil paint. | No. | 70 |  | 0
4.2 | Supply rigid polyethylene (PE) drinking water storage tank, 2000 liters capacity, food-grade, UV-stabilized, suitable for potable water storage, complete with float valve, overflow pipe (1”diam), lid, outlet ball valve 1", threaded adaptor 1"- male/female as required to suit the tank outlet and connected fittings- , and standard fittings, and all connections for rising main and distribution pipes, including all accessories and approved quality, including painting tanks with white oil paint. | No. | 100 |  | 0
4.3 | Supply rigid polyethylene (PE) drinking water storage tank, 1000 liters capacity, food-grade, UV-stabilized, suitable for potable water storage, complete with float valve, overflow pipe (1”diam), lid, outlet ball valve 1", threaded adaptor 1"- male/female as required to suit the tank outlet and connected fittings- , and standard fittings, and all connections for rising main and distribution pipes, including all accessories and approved quality, including painting tanks with white oil paint. | No. | 100 |  | 0
Total Water Tanks |  |  |  |  | 0
5 | RO units and Booster pumps
5.1 | Supply , pre-wired and tested modular packaged RO desalination unit, minimum 16 m3/day, brackish water desalination plant for max TDS salinity of raw water 5000 ppm producing water with salinity not more than 150 ppm and pH 7 for the first three years . Also the plant should be comprising of, but not limited to FEED pump, fully controlled Multimedia FRP filtration unit ,FRP cartridge filtration vessel, antiscalin dosing system and 200 liters PP tank, FRP, PN 30 high pressure vessels and RO membranes 99.7% salt rejection, HP pump, Product water filling pump and quick connections, high pressure piping, PN16 PVC piping for low pressure side, pipes, valves, gauges, Glass flow meters for raw product and brine water flows, Caustic soda dosing system, Digital EC, PH, and Turbidity meters for both raw and product water monitoring, PLC controlled electrical power and control switch board. The whole RO plant equipment shall be enclosed inside modular insulated container.All materials and equipment should be supplied in accordance with relevant clauses of specifications. Works include connecting the RO unit to the existing water supply system including all fitting, accessories, materials required to ensure full operation. | Set | 10 |  | 0
5.2 | Centrifugal Booster Pump – 3 HP: Supply a horizontal centrifugal booster pump, 3 HP (approximately 2.2 kW), 50 Hz, suitable for clean water, with a required operating capacity of 350–400 L/min at a total dynamic head of 25–35 m. Pump shall have suction and discharge connections of approximately 2", cast-iron pump casing, stainless-steel shaft, suitable corrosion-resistant impeller, mechanical seal suitable for clean water, copper-wound motor, and motor protection. The pump shall be complete with motor, base, fittings, valves, electrical connections, testing and commissioning, and all accessories required for a complete and operational installation. | Unit | 10 |  | 0
5.3 | Centrifugal Booster Pump – 4 HP: Supply a horizontal centrifugal booster pump, 4 HP (approximately 3.0 kW), 50 Hz, suitable for clean water, with a required operating capacity of 400–450 L/min (24–27 m³/h) at a total dynamic head of 30–40 m. Pump shall have suction and discharge connections of approximately 2", cast-iron pump casing, stainless-steel shaft, suitable corrosion-resistant impeller, mechanical seal suitable for clean water, copper-wound motor, and motor protection. The pump shall be complete with motor, base, fittings, valves, electrical connections, testing and commissioning, and all accessories required for a complete and operational installation. | Unit | 10 |  | 0
Total Booster Pumps |  |  |  |  | 0
6 | Generators and Trailer
6.1 | Supply, Prime Diesel Generator Set 25KVA to 30 KVA, 3 PH, 400V, 50HZ, 1500rpm with original acaustic proof sound attenuation enclosure with built in fuel day tank enough to cover 24 hours of operations, all to be made from same manufacturer including control cable XLPE, Cu Cable according to the following: generator mounted electronic modular control main panel , main circuit breaker exhaust muffler, original Sound Proof Generator Attenuator Canopy, flexible fittings, sensor heat unit, under voltage relay over voltage relay ,voltage regulator, speed control , unit oil pressure, phase sequences, phase failure, all measurement instrument, alternator, mounting arrangement, anti-vibration ,fuel water separator filter, one set of tow lead acid starting batteries, automatic battery charger, internet access point (Ethernet) and GSM modem maintenance & reporting, earthing manhole for Neutral and Masse (RESISTANCE LESS THAN 5 OHMS) ,and accessories and relative connections as per engineer approval. | Set | 10 |  | 0
6.2 | Supply, Prime Diesel Generator Set 16 KVA, 3 PH, 400V, 50HZ, 1500rpm with original acaustic proof sound attenuation enclosure with built in fuel day tank enough to cover 24 hours of operations, all to be made from same manufacturer including control cable XLPE, Cu Cable according to the following: generator mounted electronic modular control main panel , main circuit breaker exhaust muffler, original Sound Proof Generator Attenuator Canopy, flexible fittings, sensor heat unit, under voltage relay over voltage relay ,voltage regulator, speed control , unit oil pressure, phase sequences, phase failure, all measurement instrument, alternator, mounting arrangement, anti-vibration ,fuel water separator filter, one set of tow lead acid starting batteries, automatic battery charger, internet access point (Ethernet) and GSM modem maintenance & reporting, earthing manhole for Neutral and Masse (RESISTANCE LESS THAN 5 OHMS) ,and accessories and relative connections as per engineer approval. | Set | 10 |  | 0
6.3 | Supply, manufacture, and fabricate a hot-dip galvanized two-wheel modular trailer with technical specifications: - Fixed drawbar fits behind any vehicle with a dimensions L x W, ( Max. 1800 x 1000 mm), - Tires: Off-road capable, heavy-duty tires. - Hitch Type: Ball or pintle hitch for towing compatibility. The height is 500~550mm. - Qty no.2, Axles with an inertia brake. - Qty no.2, Adjustable rear hand jacks. - Fixed drawbar Height (592 mm – 1166 mm). - Supply and manufacture of wings for wheels. - Supply and installation of wheel chocks (wedges) on the trailer wings. - Hot dip galvanized generator frame and standard coupling (tow ball or DIN eye 40mm). - Lighting System: Reflectors and indicators. | Unit | 10 |  | 0
Total Generator and Trailer |  |  |  |  | 0
Total Localized Water Supply System at IDP Camps |  |  |  |  | 0